## Slide 1: Title: “Developing a Capacity Sizing and Energy Management Model for a Hybrid Photovoltaic-Hydrogen Grid-connected Building Scenario”
Presented by: Ayatte I. Atteya
Supervised by: Dr. Dallia Ali - Dr. Mamdud Hossain
School of Engineering, Robert Gordon University (RGU)

## Slide 2: Outline
Introduction
Green Hydrogen Energy Storage
Rationale of the proposed Research
The proposed hybrid PV-H2 system for grid-connected buildings
Case Study
Capacity sizing of the proposed system components
Energy Management Model of the proposed system components
Simulation Results
Conclusion

## Slide 3: Introduction
Chart: UK Greenhouse Gases (GHG) Emissions by sector 1990-2020
| 1990 | 1995 | 2000 | 2005 | 2010 | 2015 | 2020
Energy Supply | 280.7 | 238.8 | 224.2 | 232.7 | 208.8 | 146.6 | 85.3
Business | 113.4 | 111.1 | 113.6 | 105.6 | 89.8 | 83.4 | 74.1
Transport | 129.6 | 131 | 134.8 | 137.7 | 126 | 124.9 | 99.8
Residential | 80.4 | 82 | 89.4 | 86.2 | 87.9 | 67.6 | 66.6
Agriculture | 54.1 | 53.4 | 51.2 | 49.3 | 45.9 | 46.5 | 45.1
Industrial | 60.4 | 51.4 | 27.5 | 21 | 12.8 | 12.7 | 9.5
Waste management | 65.1 | 67.8 | 61.4 | 47.7 | 28.6 | 19.5 | 17.8
Public | 13.3 | 13.2 | 12.1 | 11.2 | 9.5 | 8 | 7.4
Land use | 13.2 | 10.8 | 8.3 | 5.5 | 3.7 | 3.2 | 3.8
50%
1990-2020
%Change
In June 2019, the parliament passed a new legislation requiring the UK to bring down all greenhouse gas emissions (GHG) by 100% by 2050, compared to1990 levels.
The energy supply sector has accounted for 70% of the overall reduction in UK GHG emissions since 1990.

## Slide 4: Introduction
Chart: 2020 UK GHG Emissions by Sector
| Transport | Energy Supply | Business | Residential | Agriculture | Waste management | Others
2020 UK GHG emissions by sector | 24 | 21 | 18 | 16 | 11 | 4 | 5
Chart: 2020 UK Electricity Generation by Fuel
| Natural Gas | Renewables | Coal | Oil and other fuels | Nuclear | Hydro
2020 UK Energy Supply Mix | 111.4 | 127.8 | 5.5 | 10.2 | 50.3 | 6.8
Energy Supply Sector has been the second largest contributor to GHG emissions in 2020 after transport sector, constituting 21% of total GHG emissions.
The share of renewable energy mix is required to increase by more than twice its current amount to achieve the Zero-Carbon ambition.

## Slide 5: Introduction
Integration of Energy Storage Systems
Suggested Solution
Charging Storage during hours of low demand
Discharging storage during hours of high demand
Generation profile without energy storage
Generation profile with energy storage
Fossil-fuel spinning reserves running without energy storage
The admission of renewable energy systems into the grid is subject to significant variability due to their intermittency, requiring central generations to cover any transient variation between renewable power input and consumer demand.
Improvement of Power Plant Profile with Energy Storage

## Slide 6
Green Hydrogen Energy Storage Systems
H2 Gas
H2 Liquid
Solid-state
H2 Storage System
H2O
O2 Output
H2 for other uses
H2 Production
H2 Storage
H2 Implementation
Electrical Energy Input
Electrical Energy Output
By-Products

## Slide 7
Rationale of the Proposed Research
The integration of Renewables into Electrical Power Systems brings major technical challenges which can be addressed by integrating Green Hydrogen Energy Storage (HES); however, integrating HES requires:
System Sizing
Operation Scheduling
Meeting the energy demands
Mitigating the intermittency of renewable energy
Minimizing the GHG emissions
Scheduling the operation of the hydrogen system components with other parts of the electrical system

## Slide 8
The Proposed Hybrid Photovoltaic-Hydrogen Energy System within a Grid-Connected Building Scenario
Photovoltaic (PV)
H2 Electrolyzer
H2 Storage
Fuel Cell
Discharging
Surplus Energy
(Non-utilized solar energy)
The stored solar excess energy
Utility Grid
RGU Campus Load Demands
Solar energy generation consumed by load demand
Data of Solar irradiation and temperature
Grid import to cover deficit in green energy
Charging
The Proposed Hybrid PV-H2 Energy System
(To be sized)
Notes: The proposed system will be based on PV and H2 Storage systems. During hours of high PV production, the excess energy from PV will be used to generate Green H2 by electrolyser, then the green H2 generated will be stored and discharged during the hours of off-peak generation and peak-load demand through a FC facility, to cover the shortage in PV production. The grid import will only take place to cover the deficit from both PV and H2 fuel cell.

## Slide 9
Case Study: Sir Ian Wood Building (SIWB) – RGU Campus
The proposed system sizing and energy management modelling has been developed for SIWB (as case study) based on its actual hourly load demand profile for the year 2020/2021
Parameter | Rating
Average Demand | 515.8 kW
Peak Demand | 738 kW
Minimum Demand | 340 kW
Total Annual Demand | 4.518 GW

## Slide 10
Design Specifications of PV Facility currently installed in RGU Campus | 
Panel Orientation | Facing South (Azimuth: 0°)
Pitch Angle | 15°
Solar PV Module Type | SI-Mono X Neon 300 W PV Panel
Number of PV panels installed | 100
Total PV Installed Capacity | 30 kW
Inverter Type | Power-One TRIO-27.6TL S2X Inverter
Number of installed inverters | 1
Simulating the Building Currently Installed PV Capacity

## Slide 11
Analysis of PV Facility currently installed in RGU | 
Total Solar Energy Supplied to Load Demand | 26.47 MWh
Total Load Energy Consumption | 4518 MWh
% Solar Energy Supplied to Load Demand | 0.58 %
2.42 kWh/kW/day x 30 kW x 365 days = 26.47 MWh
Total useful Solar Energy Production at the output of PV inverter
Solar Energy fed to load demand
Monthly Load Energy consumption
Simulating the Building Currently Installed PV Capacity
Notes: The results of PVSyst simulation has shown that the PV system currently installed is only able to supply 0.6% from total load demands

## Slide 12
The size of the proposed PV capacity can be calculated based on the PV capacity factor, defined as the percentage of the average output power from the PV to the rated power of PV module:
Sizing of the Proposed PV System Capacity
The PV capacity factor can be estimated by measuring the ratio of average actual solar irradiation to the solar irradiation at Standard Test Conditions
PVGIS Data of Hourly Solar Irradiation over one-year
Chart: Hours of the year
Chart: Hours of the year

## Slide 13
2.652 kWh/kW/day x 4310 kW x 365 days 4172 MWh
Total useful PV Production at the output of PV inverter
Modelling and Simulation of the Proposed PV System Capacity with no H2 Energy Storage
PVSyst Simulation Results - Monthly Solar energy production by the proposed PV capacity
PVSyst Simulation Results – Performance of the proposed grid-connected PV capacity in feeding load demands with no H2 energy storage

## Slide 14
Analysis Results of the Proposed PV System Capacity with no H2 energy Storage
Chart: Annual Contribution of the proposed grid-connected PV System in feeding load demands
| %Load supplied by PV | %Grid import
2020 UK GHG emissions by sector | 1577 | 2941
Chart: Annual Utilization of the proposed PV system capacity
| %Load supplied by PV | %Grid import
2020 UK GHG emissions by sector | 1577 | 2595

## Slide 15
Sizing of the Proposed H2 Electrolyser
The electrolyser can be sized as 50% of the proposed PV capacity to compensate for the level of underutilization during the hours of low availability of solar energy.
Satisfying the proposed Size of H2 Electrolyser
Parameter | Rating
Average H2 Electrolyser Capacity | 
Average H2 Volume Production | 
Average H2 mass Production | 
H2 Mass Flow Rate per unit capacity | 
H2 Electrolyser Target Pressure | 
Parameter | Rating
Average H2 Electrolyser Capacity | 
Average H2 Volume Production | 
Average H2 mass Production | 
H2 Mass Flow Rate per unit capacity | 
H2 Electrolyser Target Pressure | 
NEL A1000 H2 electrolyser (A-Series stacked together)

## Slide 16
Sizing of the Proposed H2 Fuel Cell
The H2 fuel cell has been sized to cover the maximum power deficit that can occur by the proposed PV capacity during the hours of minimum solar production.
PVSyst Simulation Results of Solar Energy Production at the output of PV Inverter during the month of December
30th December
Day at which occurs minimum PV Production (56 kWh daily production)
A 500-kW closest standard size of fuel cell capacity can be considered, enough to cover the average load demand during the day of min PV production
Comparison of Solar Energy output at PV inverter and Actual Load Demand during 30th December

## Slide 17
Based on the maximum permissible working pressure of the selected H2 electrolyser (200 bar), a BOC Manifold 15-Cylinder Pallet (MCP) with the following specifications can be selected:
Sizing of the Proposed H2 Storage Tank
Target Pressure
Maximum Storage Capacity
The suitability of the selected H2 tank is verified through the thermodynamic model of H2 accumulation inside the tank, considering pressure build-up and pressure decrease during charging and discharging processes of H2 tank over the year.
Volume of H2 tank

## Slide 18
Sizing Summary of the Proposed Hybrid PV-H2 Energy System
Component |  | Rating
PV System | Proposed Capacity | 4.31 MW
 | PV Modules | 14368 Modules, 300 W each
 | Modules connection | 449 strings x 32 in series
 | PV inverters | 4 units, 1000 kW each
H2 Electrolyser | Rated Capacity | 3.275 MW
 | H2 Mass Flow Rate | 0.0216 kg/h/kW
 | Target Pressure | 1-200 bars
H2 Fuel Cell | Rated capacity | 500 kW
H2 storage tank | Tank Volume | 132 m3
 | Mass Storage Capacity | 1331 kg
 | Target Pressure | 200 bars
To schedule the operation of proposed components and the utility grid in feeding the building demands
Energy Management Model
Running on an hourly-basis
over the year

## Slide 19
Energy Management Model – Flowchart
START
Initialization of component sizing developed for the Proposed Hybrid PV-H2 Energy System
Data input of hourly load demand profile and hourly solar irradiation
t=1
Calculate hourly PV Output Power:
A
Apply Scenario of PV excess
B
Apply Scenario of PV Deficit
END
YES
NO
YES
NO

## Slide 20
Energy Management Model – Scenario of PV Energy Excess
YES
NO
NO
YES
A
Calculate mass of H2 generated:
Calculate no. of H2 moles generated:
Calculate no. of H2 moles present in the tank:
Calculate the operating pressure of H2 tank:
Allow charging of H2 tank and update the mass status of H2 tank:
Stop filling H2 tank
Calculate the Non-utilized PV excess
Set:
Set:
Main Function
Evaluate mass of H2 to be sold to grid

## Slide 21
Energy Management Model – Scenario of PV Energy Deficit
B
Calculate mass of H2 to be consumed:
Allow discharging of H2 tank and update the mass status of H2 tank:
Calculate no. of H2 moles consumed by fuel cell:
Update no. of H2 moles present in the tank:
Calculate the operating pressure of H2 tank:
Set:
Update based on mass of H2 available in the tank
Calculate the power that needs to be imported from grid
Calculate the power that needs to be imported from grid
Main Function
YES
NO
YES
NO

## Slide 22
Simulation Results of Hybrid PV-H2 Energy System
Simulation Results over one-year timescale
Simulation Results over one Summer week
Hours of high PV production
H2 Charging
Hours of low PV production
Electrolyser “ON”
Pressure decrease
H2 discharging
Fuel Cell “ON”
Pressure rise

## Slide 23
Simulation Results over one Winter week
Simulation of Hourly status of H2 tank and the associated operating pressure during the month of June
Simulation Results of Hybrid PV-H2 Energy System

## Slide 24
Chart: Annual Contribution of the proposed grid-connected PV-H2 System in feeding load demands
| %Load supplied by PV | %Load supplied by H2 fuel cell | %Grid import
2020 UK GHG emissions by sector | 1697 | 950 | 1871
Chart: Annual utilization of the proposed PV system capacity
| %PV power fed to load | %PV power electrolysed | %Non-utilized PV excess
2020 UK GHG emissions by sector | 1697 | 2365.675 | 111.1968
Monthly power exchange of the proposed Grid-connected PV-H2 System in supplying the load demands
Simulation Results of Hybrid PV-H2 Energy System

## Slide 25
A Capacity sizing and Energy Management Modelling has been developed for the proposed hybrid Photovoltaic-Hydrogen Energy System for grid-connected building scenario to support the building sector decarbonization while ensuring a reliable system operation
The results have shown a maintained energy balance between the renewable generation, load consumption, green hydrogen production by electrolyser and consumption by fuel cell, with less contribution from the utility grid throughout the year.
The integration of the proposed Hydrogen Energy Storage System has increased the total contribution of green energy in feeding the building load demand by 21%, while improving the utilization of the proposed PV system capacity by 59%.
Conclusion

## Slide 26
Any Questions?