## Slide 1: ECONOMIC ASSESSMENT OF ENERGY STORAGE SYSTEMS
Ross Gazey, BSc(Eng)Hons., MPhil, MIET
PhD Research Student, Robert Gordon University
IET Renewable Power Generation Conference 2011
5-8 September 2011

## Slide 2: Overview
Introduction
Background
Energy Storage System (ESS) Summary
Hydrogen ESS
Modelling
Results.

## Slide 3: Introduction
PEC
ETP
RGU
Strathclyde
Research Output
Research Partners

## Slide 4: Introduction
Supervisory Team:
  Dr. Dallia Ali (RGU)
  Dr. Daniel Aklil (PEC)
  Dr. Stephen Finney (Strathclyde)
  Ross Gazey (RGU - PhD Research)
Acknowledgements to Energy Technology Partnership (ETP), Strathclyde University, Pure Energy Centre, and the Robert Gordon University IDEAS research centre

## Slide 5: Background
Within Scotland ambitious national targets are focused on achieving renewable generation of 80% by the year 2020
Existing electrical infrastructure is becoming increasingly constrained
Department of Energy & Climate Change announced:
  “In future we need greater electrical energy storage facilities and greater interconnection with our EU neighbours so that excess energy supplies can be sold or bought where required”

## Slide 6: Energy Storage Systems (ESS)
Typical Elements of Energy Storage Systems
Energy Conversion
Energy
Storage
Medium
Energy Conversion
Electrical Energy Input
Electrical Energy Output
Energy Storage System

## Slide 7: ESS Characteristics
Depth of Discharge (DoD)
  How much energy can we take out
Duration – Storage Capacity (kWh)
  How much can we store and for how long
Charge/Discharge rates
  How fast can we replenish or remove energy
Turn Around Efficiency
  How much is lost on the journey through
How much does it cost
  Capex
  Opex

## Slide 8: Summary of ESS costs*
Technology | €/kWh | €/kW | Life Time (years) | Efficiency (%)
Pumped Hydro | 10-20 | 500-1500 | 40-80 | 65-80
Fuel Cell | 2-15 | 300-1000 | 10-20 | 35-45
Battery | 210-250 | 125-150 | 10-15 | 75-85
Flywheel | 150-200 | 200-250 | 20 | 90
CAES | 3-5 | 300-600 | 20-40 | 80-85
*Values taken from literature:
  A. Marshall, “Electricity Storage Struggles to add up”, Ends Report 435, April 2011.
  D. Connolly, “A Review of Energy Storage Technologies For the integration of fluctuating renewable energy”, University of Limerick, August 2009
  D.Lumb, “Energy Storage & Renewables, is it an uphill struggle?”, Edison Mission Energy.
  J.K Kaldellis etall, “Techno-economic comparison of energy storage systems for islands autonomous electrical networks” Renewable & sustainable energy reviews 13 (2009).

## Slide 9: Hydrogen ESS cost
Economic Costs Data* | 
Hydrogen ESS Capex | 
Electrolyser (€/kW) | € 2,500.00
Storage (€/kWh) | € 77.00
Fuel Cell (€/kW) | € 4,000.00
Annual Hydrogen ESS Opex | 
Electrolyser (€/kW) | € 50.00
Storage (€/kWh) | € 2.00
Fuel Cell (€/kW) | € 100.00
Energy cost (€/kWh) | € 0.06
Energy Costs | 
Constrained cost (€/MWh) | € 238.89
Generation value (€/MWh) | € 61.11
cost differential (€/MWh) | € 177.78
*Courtesy of the Pure Energy Centre

## Slide 10: Hydrogen & Conventional Energy Storage
Energy In (€)
Energy Out (€)
H2 Out (€)
O2 Out (€)
Hydrogen Energy Storage
Conventional Energy Storage
Energy In (€)
Energy Out (€)

## Slide 11: Hydrogen ESS
Electrolyser
H2
Energy
Storage
Fuel Cell
H2
H2
Electrical Energy Input
e
Elements for complete Hydrogen Energy storage system
e = electrical energy
H2 = hydrogen gas
Electrical Energy Output
e
Oxygen Output
H2 For other use
H2
H2
O2

## Slide 12: Hydrogen ESS
What is an Electrolyser?
  An Electrochemical device the converts electrical energy and pure water into hydrogen
  By-products are:
    Oxygen (O2)
    Waste heat (Pth)
  Typical Efficiency Range 55% to 90%
H2O
Z
Pth
Pe
H2
O2
Electrolyser

## Slide 13: Hydrogen ESS
What is a Fuel Cell?
  An Electrochemical device the converts energy in hydrogen into electricity
  By-products are:
    Water vapour (H2O)
    Waste heat (Pth)
  Typical Efficiency Range 40% to 60%
Pth
Pe
H2
H2O
O2 (Air)
Fuel Cell

## Slide 14: Modelling ESS cost
The developed ‘Levelised’ ESS cost model considered:
  Total cost of ownership
    ISCt = Invested Storage Capital in year (t)
    SOMt = Storage Operation and Maintenance costs in year (t)
    ECt = input energy cost (t)
  Total value of output
    EOt = Value of sold energy in year (t)
    H2t = Value of sold hydrogen gas year (t)
    O2t = Value of sold Oxygen gas in year (t)
  Annual Discount rate of 10% considered (r)
  20 year operation life considered for H2 (n)

## Slide 15: Modelling ESS cost
Levelised Cost of Storage (LSC)
    ISCt = Invested Storage Capital in year (t)
    SOMt = Storage Operation and Maintenance costs in year (t)
    ECt = input energy cost (t)
    EOt = Value of sold energy in year (t)
    H2t =Value of sold hydrogen gas year (t)
    O2t =Value of sold Oxygen gas in year (t)
    r =Annual Discount rate of 10%
    n =20 year operation life considered for H2

## Slide 16: Modelling ESS cost
Market Data* | 
O2 Sale (€/Tonne) | € 3,000.00
H2 Sale (€/Tonne) | € 5,000.00
Electricity sale (€/MWh) | € 177.78
Discount rate (r) | 10%
*Courtesy of the Pure Energy Centre

## Slide 17: Modelling ESS cost
Considered Scenarios:
No FC - (no energy sale), 100% 02 & H2 gas sold
100% energy sale - 3MW FC, 100% 02 sold, no H2 sale
50% O2 & H2 gas sold, 50% H2 sold as energy through a 3MW FC
No FC - (no energy sale), no 02 sold, 100% H2 sold
100% Energy sold (3MW FC), no O2 nor H2 sold

## Slide 18: Results
Chart: LSC (€/unit output)
| Scenario A | Scenario B | Scenario C | Scenario D | Scenario E
LSC (€/kWh) | 0.20637 | 0.32373 | 0.51992 | 0.90821 | 1.9535
only electricity output
only H2 & O2 output

## Slide 19: Results
Chart: LSC (€/unit output)
| Scenario A | Scenario B | Scenario C | Scenario D | Scenario E | NiCd Battery | NaS Battery | Vanadium Redox battery | Pumped hydro | CASE
 | 0.20637 | 0.32373 | 0.51992 | 0.90821 | 1.9535 | 0.57552 | 0.17335 | 0.19415 | 0.090142 | 0.06934
How does H2 Compare with other technologies
No O2
O2 Utilised

## Slide 20: Conclusion
Electrolysis as a network deferrable balancing load has the potential to offer a cost effective solution
H2 technology is getting close to other electrochemical energy storage technologies where otherwise ‘vented’ O2 is utilised.
When looking at electricity only, cost of H2 technology has to reduce to become as competitive with other ESS.